## Instructions
ANNEX 4 - Technical Compliance Tables
Project: Renovation and modernization of crisis management spaces of the MFA
How to complete this Annex:
1. For each requirement, fill in column F with the make, model and the actual technical values of the offered product.
2. In column D and E “Bidder's Response” write Yes or No. If No, describe the discrepancy in column E.
3. Equivalent products are accepted if their performance is not lower than the requirement and compatibility with the connected systems is maintained. The reference models are provided solely to define the required level of quality, performance, and functionality.
4. Attach the datasheet / catalogue page for each equipment item, in the order of the sheets, marked with the item number (e.g. “IVC - Item 3”).
5. Quantities are governed by the BoQ. This Annex confirms technical compliance only.

## SA_MASI
ANNEX 4 - SA_MASI Technical Compliance Sheet
No. | Parameter | Specification / minimum technical requirement | Bidder’s response |  | Technical Compliance (indicate proposed technical specifications)
|  |  | Yes, we comply | No, we do not comply (indicate discrepancies)
Project: Renovation and modernization of crisis management spaces of the MFA
1 | Fire-rated doors EI30
| Purpose / location | Fire-rated complete door assemblies for rooms and evacuation/fire compartments as shown in architectural drawings and MASI. Opening direction and exact location shall be as indicated in the final architectural drawings.
| Fire performance | Minimum EI30 as per EN 1634-1 standard
| Type / dimensions | As per final door schedule and drawings: • U-1 – external full fire-rated door EI30, aluminium, opening size 1200 × 2100 mm • U-2 – full fire-rated door EI30, HPL, opening size 1200 × 2100 mm • U-6 – glazed fire-rated door EI30, HPL with fire-rated glass, opening size 1200 × 2200 mm • U-8 – external full fire-rated door EI30, aluminium, opening size 1200 × 1950 mm Color(s) to be confirmed with designer during the implementation stage.
| Compatibility | Compatible with access control hardware where required, without reducing fire rating or evacuation function.
| Bidder evidence | Datasheet/catalogue and fire-rating evidence for the complete door assembly.
2 | Soundproof doors
| Purpose / location | Soundproof complete door assemblies where indicated in the architectural door schedule. Opening direction and exact location shall be as indicated in the final architectural drawings
| Soundproof performance | Rw ≥ 37-42 dB as per ISO 717-1
| Type / dimensions | As per final door schedule and drawings: • U-4 – full soundproof door, HPL, opening size 1000 × 2100 mm • U-5 – full soundproof door, HPL, opening size 1200 × 2100 mm • U-9 – full soundproof door, HPL, opening size 950 × 1500 mm Color(s) to be confirmed with designer during the implementation stage.
| Compatibility | Installation shall not create acoustic bridges or unsealed gaps.
| Bidder evidence | Datasheet/catalogue indicating construction and declared soundproof performance.
EQUIVALENCE ACCEPTANCE RULES / TECHNICAL TOLERANCES – SA_MASI
No. | Parameter category | Acceptance rule / minimum requirement | Bidder’s response | Yes/No compliance | Technical Compliance / comments
1 | Fire-rated / soundproof assemblies | No reduction accepted for EI/E/EW class, reaction-to-fire class or soundproof performance. Door/fire-stop equivalence shall be proven for the complete tested assembly, including leaf, frame, seals, closer, hinges, hardware and installation method. |  |  | Equivalent finishes or doors require datasheets, certificates/test reports and samples where requested.

## RAC
ANNEX 4 - RAC Technical Compliance Sheet
No. | Parameter | Specification / minimum technical requirement | Bidder’s response |  | Technical Compliance (indicate proposed technical specifications)
|  |  | Yes, we comply | No, we do not comply (indicate discrepancies)
Project: Renovation and modernization of crisis management spaces of the MFA
1 | Wastewater pumping stations
| Function | Basement wastewater collection and pumping stations, complete and fully operational, suitable to handle household wastewater, including from sinks and toilets.
| Main capacity | Tank capacity - approx. 250 l and Pump motor power - approx. 1.1 kW
| Type | Similar quality and performance to SAR 250 TRITUSm 1.1 kW
| Controls | Automatic level control, dry-run/overload protection and alarm/fault feedback.
| Bidder evidence | Datasheet, pump curve and confirmation of wastewater suitability.

## IVC
ANNEX 4 - IVC Technical Compliance Sheet
No. | Parameter | Specification / minimum technical requirement | Bidder’s response |  | Technical Compliance (indicate proposed technical specifications)
|  |  | Yes, we comply | No, we do not comply (indicate discrepancies)
Project: Renovation and modernization of crisis management spaces of the MFA
1 | RA1 ventilation unit
| Function | Heat recovery air handling / ventilation
| Airflow (supply/exhaust) | L=1850/1550 m³/h
| External Static Pressure (supply/exhaust) | P=300/250 Pa
| Power supply / motor power | 1~230 V; reference total nominal electrical consumption of complete RA1 unit approx. 9.2 kW, including electric heater, EC fans, rotary heat recovery drive and integrated automation.
| Heat recovery / heater | Rotary heat recovery; electric heater, 3~400 V, approx. 7.5 kW; heating temperature range indicated in design: -16°C / +9°C and +9°C / +20°C.
| Cooling / recovery section | Plate heat exchanger, 35°C / 27°C, as indicated in design.
| Thermal efficiency | 73%
| Supply line | Sound attenuator SMN 620x400 M5 filter SCF 620x400
| Exhaust line | Sound attenuator SMN 620x400 External grille 800x600
| Overall dimensions (LxWxH) | 2400x850x1200 mm
| Bidder evidence | Official datasheet and AHU selection sheet confirming airflow, pressure, filtration, heater capacity, heat-recovery performance, SFP/fan efficiency, acoustic data, CE/DoC and O&M documentation.
2 | RA2 ventilation unit
| Function | Heat recovery air handling / ventilation
| Airflow (supply/exhaust) | L=3300/3300 m³/h
| External Static Pressure (supply/exhaust) | P=380/320 Pa
| Power supply / motor power | 3~400 V; reference total nominal electrical consumption of complete RA2 unit approx. 15.1 kW, including electric heater, EC fans, rotary heat recovery drive and integrated automation.
| Heat recovery / heater | Rotary heat recovery; electric heater, 3~400 V, approx. 11.1 kW; heating temperature range indicated in design: -16°C / +11°C and +11°C / +20°C.
| Cooling / recovery section | Plate heat exchanger, 35°C / 27°C, as indicated in design.
| Thermal efficiency | 73%
| Supply line | Sound attenuator SMN 720x450 M5 filter SCF 720x450
| Exhaust / intake line | Sound attenuator SMN 720x450 External grille 1200x600
| Overall dimensions (LxWxH) | 2400x950x1300 mm
| Bidder evidence | Official datasheet and AHU selection sheet confirming airflow, pressure, filtration, heater capacity, heat-recovery performance, total electrical load, SFP/fan efficiency, acoustic data, CE/DoC and O&M documentation.
3 | RA3 ventilation unit
| Function | Heat recovery air handling / ventilation
| Airflow (supply/exhaust) | L=3075/2800 m³/h
| External Static Pressure (supply/exhaust) | P=380/320 Pa
| Power supply / motor power | 3~400 V;reference total nominal electrical consumption of complete RA3 unit approx. 15.1 kW, including electric heater, EC fans, rotary heat recovery drive and integrated automation.
| Heat recovery / heater | Rotary heat recovery; electric heater, 3~400 V, approx. 11.1 kW; heating temperature range indicated in design: -16°C / +9.5°C and +9.5°C / +20°C.
| Cooling / recovery section | Plate heat exchanger, 35°C / 27°C, as indicated in design.
| Thermal efficiency | 73%
| Supply line | Sound attenuator SMN 720x450 M5 filter SCF 720x450
| Exhaust / intake line | Sound attenuator SMN 720x450 External grille 1200x600
| Overall dimensions (LxWxH) | 2400x950x1300 mm
| Bidder evidence | Official datasheet and AHU selection sheet confirming airflow, pressure, filtration, heater capacity, heat-recovery performance, SFP/fan efficiency, acoustic data, CE/DoC and O&M documentation.
4 | DF1 smoke exhaust fan
| Fan type | Radial fan.
| Airflow / pressure | L=20000 m³/h, P=650 Pa.
| Power supply / motor power | 3~400 V; N=11.00 kW.
| Set includes | Smoke exhaust damper FID K3 900x700
| Bidder evidence | Fan datasheet and performance curve confirming duty point and smoke extraction suitability. For smoke-control/desfumare function, provide EN 12101-3 certificate/classification and CE/DoP where applicable; ordinary ventilation fan evidence is not sufficient.
5 | SP.DF1 pressurization fan
| Fan type | Radial fan.
| Airflow / pressure | L=14000 m³/h, P=900 Pa.
| Power supply / motor power | 3~400 V; N=7.50 kW.
| Set includes | Smoke exhaust damper FID K3 800x500 Non-return damper Ø630.
| Bidder evidence | Fan datasheet and performance curve confirming duty point and operating modes. For smoke-control/pressurization function, provide EN 12101-3 or other applicable fire-safety certification where required by the final fire scenario, plus CE/DoP where applicable.
6 | SP.DF2 pressurization fan
| Fan type | Radial fan.
| Airflow / pressure | L=12000 m³/h, P=800 Pa.
| Power supply / motor power | 3~400 V; N=7.50 kW.
| Operating modes | Reduced mode for pressure control with closed door and maximum mode for open door condition, as per approved design/fire scenario.
| Set includes | Smoke exhaust damper FID K3 1000x500 Non-return damper Ø630.
| Bidder evidence | Fan datasheet and performance curve confirming duty point and operating modes. For smoke-control/pressurization function, provide EN 12101-3 or other applicable fire-safety certification where required by the final fire scenario, plus CE/DoP where applicable.
7 | Auxiliary exhaust fans A1/A2
| Function | Auxiliary duct exhaust fans for local ventilation duties as per IVC design; kept as one grouped major item only if required for system performance/commissioning.
| Exact project reference | A1: 1 pc duct fan, L=300 m³/h, P=180 Pa, 1~230 V, N=0.16 kW; includes RMN 200/10 sound attenuator, Ø200 non-return damper and Ø315 external grille.
A2: 1 pc duct fan, L=275 m³/h, P=150 Pa, 1~230 V, N=0.16 kW; includes RMN 200/10 sound attenuator, Ø200 non-return damper and Ø315 external grille.
| Bidder evidence | Datasheets, fan curves, CE/DoC, ErP/Ecodesign evidence where applicable, acoustic data and commissioning/test procedure.
8 | VRF outdoor unit ODU1
| Function | Outdoor VRF unit for air-conditioning system.
| Power supply / electrical power | 3~400 V; reference absorbed/input power N≈10.30 kW.
| Cooling capacity | Qr ≥ 33.5 kW
| Heating capacity | Qh ≥ 37.5 kW
| Refrigerant | R410A or R32
| Bidder evidence | VRF unit datasheet confirming compatibility with all indoor units, Qr/Qh, electrical input, refrigerant quantity, CE/DoC and O&M documentation.
9 | VRF indoor units IDU1.1–IDU1.7
| Function | Indoor VRF units compatible with ODU1, including cassette and wall-mounted units and all accessories required for complete operation.
| Quantity / types | 5 pcs cassette-type indoor units IDU1.1–IDU1.5 with drainage pump; 2 pcs wall-mounted indoor units IDU1.6–IDU1.7.
| Capacities | Cassette units: Qr ≥ 5.6 kW and Qh ≥ 6.3 kW per unit. Wall-mounted units: Qr ≥ 2.2 kW and Qh ≥ 2.5 kW per unit.
| Power | 1~230 V; reference N≈0.04 kW per indoor unit
| Refrigerant | R410A or R32
| Drenage Pump | Similar to Sauermann Si-30 (only for cassette-type indoor units )
| Bidder evidence | Indoor unit datasheets, VRF compatibility table, selection report, noise data, CE/DoC and O&M documentation.
GENERAL ACCEPTANCE REQUIREMENTS – IVC
No. | Parameter | Specification / minimum technical requirement | Bidder’s response |  | Technical Compliance (indicate proposed technical specifications)
A | Selection sheets / technical parameters | For RA1/RA2/RA3, fans, VRF and related equipment, bidder shall submit manufacturer selection sheets showing airflow, available external static pressure, duty point, motor/input power, SFP/fan efficiency, acoustic data, dimensions, weight, filters, heat recovery, heating/cooling capacity and operating conditions.
B | Certification / standards | Bidder shall submit CE/EU Declaration of Conformity and applicable product certificates. AHU/ventilation evidence shall include EN 1886, EN 13053, EN 308, ISO 16890 and EN 17166 or equivalent where applicable. Smoke-control/ exhaust fans shall be certified according to EN 12101-3 with the required temperature/time class; ordinary ventilation certificates are not sufficient for smoke-control duty.
C | Filters and components | Filter classes, sound attenuators, dampers, grilles, actuators and accessories shall match the final design and shall not reduce airflow, pressure, acoustic or fire-safety performance. For fire/smoke dampers provide EN 15650 / EN 12101-8, EN 1366 and EN 13501 classification where applicable.
D | Electrical coordination | Any deviation of total electrical load shall be justified by the AHU selection report and shall not require changes to designed electrical supply, protection devices, cable sizing or operating safety.

## EEF_IEI
ANNEX 4 - EEF_IEI Technical Compliance Sheet
No. | Parameter | Specification / minimum technical requirement | Bidder’s response |  | Technical Compliance (indicate proposed technical specifications)
|  |  | Yes, we comply | No, we do not comply (indicate discrepancies)
Project: Renovation and modernization of crisis management spaces of the MFA
1 | Main electrical panels and distribution boards | Scope: AAR+IRD, TGD, PDG, PDV, PI1, PI2, PI3, complete with enclosures, DIN/N/PE bars, wiring, terminals, labels, SPD/RCD/RCBO/protective devices, earthing/bonding provisions and accessories.
| Function | Main and distribution electrical panels shall be supplied and installed as per approved EEF/IEI single-line diagrams and final panel schedules: AAR+IRD, TGD, PDG, PDV, PI1, PI2 and PI3.
| System | 400/230 V, TN-C-S earthing system; design indicators: calculated power approx. 124 kW and calculated current approx. 195 A
| Dimensions | Approx. H=2000 mm, W=650+150 mm, D=400 mm.
| Rated current | Automatic transfer switch (similar to TransferPact Automatic), rated current 400 A, nominal voltage 400 V, 4 poles (4P), rotary execution, frame/casing 400 A
| Controls / indication/ protection | Automatic/manual mode, status indication and interlocking as required. The equipment shall be supplied complete with: Three-phase meter 5(10)A class 0.5s; Current transformers 200/5A, class 0.5s, U=0.66 kV; КИУ-3 contact panel; GSM/GPRS module and antenna for electric meter; Circuit breaker In=100A; MX+OF shunt trip 380–415 V; Surge Protection Device 3P+N In=30 kA Un=400 V.
| Bidder evidence | Bidder shall submit panel proposal, panel drawings/schedules, datasheets and confirmation of compliance with single-line diagrams. Manufacturer indicated in the design is not mandatory; equivalent products are acceptable only if technically equivalent and certified/accepted for use in the Republic of Moldova.
2 | Lighting fixture/luminaire, model 1
| Type | LED type (similar to PHILIPS WT120C LED40S/840 PSU L1200): 4000K, 4000lm, 36W
| Protection class | IP 65
| Bidder evidence | Bidder shall submit datasheets/certificates for luminaires, including power, IP class, light output, color temperature.
3 | Lighting fixture/luminaire, model 2
| Type | LED type (similar to PHILIPS SM136V PSU W20L120 ELB3 1x37S/840 NOC): 4000K, 4300lm, 34W
| Protection class | IP 20
| Bidder evidence | Bidder shall submit datasheets/certificates for luminaires, including power, IP class, light output, color temperature.
4 | Lighting fixture/luminaire, model 3
| Type | LED type, 600x600mm, 4000K, 1200lm, 12W
| Protection class | IP 20
| Bidder evidence | Bidder shall submit datasheets/certificates for luminaires, including power, IP class, light output, color temperature.
5 | Lighting fixture/luminaire, model 4
| Type | LED type, 1200x50mm, 4000K, 800lm, 8W
| Protection class | IP 20
| Bidder evidence | Bidder shall submit datasheets/certificates for luminaires, including power, IP class, light output, color temperature.
GENERAL ACCEPTANCE REQUIREMENTS – EEF_IEI
No. | Parameter | Specification / minimum technical requirement | Bidder’s response |  | Technical Compliance (indicate proposed technical specifications)
A | Panel documentation and FAT/SAT | For AAR+IRD, TGD, PDG, PDV, PI1, PI2, PI3 and other panels, bidder shall submit panel drawings, single-line diagrams, device schedules, enclosure details, heat/space check, wiring diagrams, labels, FAT/SAT protocols and confirmation of compliance with final approved EEF/IEI design.
B | Protective devices / coordination | Circuit breakers, RCD/RCBO, SPD, contactors, ATS/AAR and meters shall be compliant with relevant IEC/EN standards, with rated current, breaking capacity, number of poles, trip curve, residual current sensitivity, SPD rating and selectivity/coordination not lower than design.

## SI_SIn
ANNEX 4 - SI / SIn Technical Compliance Sheet
No. | Parameter | Specification / minimum technical requirement | Bidder’s response |  | Technical Compliance (indicate proposed technical specifications)
|  |  | Yes, we comply | No, we do not comply (indicate discrepancies)
Project: Renovation and modernization of crisis management spaces of the MFA - Fire alarm and gas extinguishing systems
1 | Fire alarm control panel and loop/interface equipment
| Function | Addressable fire alarm control panel for SI/SAv system and integration with SIn gas extinguishing system, with supervised loops, alarm/pre-alarm/fault modes, event logging and interface outputs.
| Design reference / capacity | Addressable and network-connectable control panel (similar to INIM Previdia216 / Previdia216R). Minimum functional capacity not lower than design: 2 loops expandable up to 16 loops, modular architecture for fire detection and gas-extinguishing control, support for internal IFM/FPM modules, event log, supervised outputs and interfaces. System shall support the designed SI/SIn quantities and future expansion without reducing certified functionality.
| Required certifications | EN 54-2, EN 54-4, EN 54-21 and EN 12094-1, or equivalent accepted standards.
| Main modules | IFMEXT internal gas-extinguishing control module; EM322AC addressable module with 2 inputs / 2 relay outputs, max. 5A/230VAC, with supervision; FPMEXT-G front LED indication module with 40 tricolour LEDs
| Bidder evidence | Bidder shall submit official datasheets, EN/CPR certificates, Declaration of Performance, EU Declaration of Conformity, compatibility/connectability evidence for all proposed panel modules and field devices, programming method and commissioning procedure.
GENERAL ACCEPTANCE REQUIREMENTS – SI_SIn
No. | Parameter | Specification / minimum technical requirement | Bidder’s response |  | Technical Compliance (indicate proposed technical specifications)
A | System compatibility package | The fire alarm and gas-extinguishing equipment shall be proposed as a compatible certified system. Bidder shall submit datasheets, CoP/CPR, DoP where applicable, EU Declaration of Conformity and compatibility/connectability evidence for control panel, modules, detectors, manual call points, sounders, power supplies and extinguishing interfaces.
Note on A4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: What about equipment for gas extinguishing system? Reply: Instalatie de extractie a fumului, Modul de stingere a incendiilor cu gaz, centrala PREVIDIA216R - could be potentially part of current sheet - up to you Reply: Model PREVIDIA216R is already referenced under line 7. Overall, this is a system with several components. Modules under line 9 include also the gas extinguishing module

## SCA
ANNEX 4 - SCA / Access Control Technical Compliance Sheet
No. | Parameter | Specification / minimum technical requirement | Bidder’s response |  | Technical Compliance (indicate proposed technical specifications)
|  |  | Yes, we comply | No, we do not comply (indicate discrepancies)
Project: Renovation and modernization of crisis management spaces of the MFA - SCA / Access Control System
1 | Access control network controllers
| Minimum capacity | Network access controller (Wiegand interface) for 2 controlled access points/doors, mounted in metal enclosure with integrated power supply, LAN connection, as per SCA design.
| Bidder evidence | Bidder shall submit official datasheet, wiring diagram, power requirements, controller capacity, software compatibility statement and warranty/service information.
2 | Biometric/card readers
| Function | Biometric fingerprint and MIFARE card readers for controlled access points as per final SCA design; two readers per door/access point where required by design, for entry/exit identification.
| Minimum requirements | Support multiple authentifications modes (card, fingerprint, and card + fingerprint), support RS-485 communication, readers shall be suitable for the Beneficiary’s access-control policy and compatible with the proposed access control controllers.
| Bidder evidence | Bidder shall submit datasheet, compatibility statement with the proposed controller, biometric/card technology description and cybersecurity/data protection information.
GENERAL ACCEPTANCE REQUIREMENTS – SCA
No. | Parameter | Specification / minimum technical requirement | Bidder’s response |  | Technical Compliance (indicate proposed technical specifications)
A | Quality / conformity documentation | For controllers, readers, locks, batteries, cables and accessories, bidder shall submit official datasheets, CE/EMC/RoHS declarations where applicable, warranty, service/support confirmation, product traceability and evidence of compatibility as a complete access-control system.
B | Cybersecurity / data protection | System shall support secure local administration, role-based access, event logging, password management and protection of biometric/personal data. Mandatory external cloud/P2P operation shall not be accepted unless expressly approved by the Beneficiary.
C | Fire and evacuation interface | Electromagnetic locks and controllers shall be configured so that emergency evacuation and fire alarm release logic are not impaired. Fail-safe behaviour, power loss response and SI/SIn integration shall be demonstrated by functional tests.

## CCTV
ANNEX 4 - CCTV Technical Compliance Sheet
No. | Parameter | Specification / minimum technical requirement | Bidder’s response |  | Technical Compliance (indicate proposed technical specifications)
|  |  | Yes, we comply | No, we do not comply (indicate discrepancies)
Project: Renovation and modernization of crisis management spaces of the MFA – CCTV / Video Surveillance
1 | IP camera
| Function | Video surveillance of protected basement areas as per final CCTV design and camera layout.
| Minimum performance | Resolution 4 MP; anti-vandal housing; motion detection; image sensor: 1/3'', lens/focal length 2.8 mm; IR min 20 m; PoE power supply max 7W; protection - IP67.
2 | NVR / recording equipment with storage
| Function | Recording, administration and playback of the CCTV/video surveillance system, compatible with the proposed IP cameras
| Minimum performance | 16 IP channels; compatible HDD 6Tb suitable for 24/7 video recording included; H.265/H.264 video formats; ONVIF; HDMI/VGA outputs; RJ-45 10/100/1000 Mbps; SATA interface; supports recording at the required camera resolution, compression, playback, event search, export and user management; motion detection
3 | PoE Switch
| Minimum performance | 16xPoE ports; 1xGigabit combo; 1xRJ-45 Gigabit; PoE power budget 130W
4 | UPS
| Minimum performance | Rack mount, 1000W, running time - up to 4h at nominal power 125W
GENERAL ACCEPTANCE REQUIREMENTS – CCTV
No. | Parameter | Specification / minimum technical requirement | Bidder’s response |  | Technical Compliance (indicate proposed technical specifications)
A | Quality / conformity documentation | For cameras, NVR, PoE switch, UPS and accessories, bidder shall submit official datasheets, certificates/declarations, warranty, service/support confirmation, product traceability and confirmation of compatibility between all CCTV components.
B | Cybersecurity / supply-chain | CCTV system shall operate locally/on-premises without mandatory dependence on external cloud, P2P, uncontrolled remote access or telemetry. Bidder shall describe firmware update policy, administrator access, password management, role-based access, logs and any remote/cloud functions, which shall be disabled unless approved.
C | Recording / storage | Bidder shall provide retention calculation for the final number of cameras using proposed resolution, fps, codec, bitrate and recording mode. HDD shall be designed for 24/7 surveillance workload and compatible with the NVR.

## TS_SCS
ANNEX 4 - TS / SCS Technical Compliance Sheet
No. | Parameter | Specification / minimum technical requirement | Bidder’s response |  | Technical Compliance (indicate proposed technical specifications)
|  |  | Yes, we comply | No, we do not comply (indicate discrepancies)
Project: Renovation and modernization of crisis management spaces of the MFA - TS / Structured Cabling System
1 | Telecommunication rack cabinet
| Project reference | Rack cabinet XL VDI 19”, 6U, 350×600×400 mm / 600×400 mm, with side panels, lock and door
2 | Rack PDU
| Project reference | Power distribution unit (PDU) for 19” cabinet with 8 IEC 60320 C13 outlets and switch
3 | Patch panel
| Project reference | 19” 1U, 24 ports, UTP RJ-45
4 | Network switches
| Project reference | 19”, 1U, 24 Ethernet ports 10/100 Mbps

## ACCEPTABLE_DEVIATIONS
ANNEX 4 – EQUIVALENT PRODUCT ACCEPTANCE RULES / TECHNICAL TOLERANCES
General Principle Acceptance of an equivalent (similar) product is based on overall compliance with the intended function, safety objectives, requirements, interoperability and lifecycle performance of the specified system. Compliance with individual parameters alone does not constitute acceptance.
Parameter category | Acceptance rule | Typical margin / limit | Conditions for acceptance | Evidence required | Risk if not controlled
Certifications / standards / fire ratings | Equal or superior only | 0% negative deviation | Applies to EN/IEC/ISO/CE/CPR/DoP/CoP/EI/E/EW/FE/E classes and safety functions | Certificates, DoP/CoP, EU Declaration of Conformity, test reports | Safety non-compliance, claims, rejection at reception
Minimum functional capacity | Minor variations may be accepted if no adverse impact | ±10% | Flow, pressure, useful capacity, number of ports/bays/loops/zones, holding force, current rating, breaking capacity | Datasheet, selection sheet, calculations | Undersized system or loss of function
Oversizing / higher performance | May be accepted if no adverse impact | Approx. +10…15% for capacity/duty where reasonable | Must not affect noise, consumption, control, balancing, space, support, maintenance or warranty | Technical justification and designer/Employer approval if material | Operational instability and increased cost
Electrical input power / consumption | Minor increase may be accepted | +10% or +0.02 kW for loads below 0.10 kW | Protections, cable sizing, UPS/battery autonomy and total energy impact must remain compliant | Load calculation / autonomy check | Overloaded circuits, reduced autonomy
Dimensions | Minor variations may be accepted if no adverse impact | ±5% | Must fit in designed space and maintain access for operation/maintenance | Dimensional drawing / installation check | Installation clashes and access problems
Weight | May be accepted if supports remain adequate | ±10% | Mounting structure, brackets, wall/ceiling supports and seismic/safety fixing must remain adequate | Weight data and fixing/support confirmation | Support failure or additional works
Noise level | Prefer equal or lower. Minor variations may be accepted if no adverse impact | 3-5 dB(A) | No negative impact on occupied/technical rooms or acoustic requirements | Acoustic datasheet / calculation | Unacceptable working conditions
Efficiency / COP / EER / SFP / energy performance | Minor variations may be accepted if no adverse impact | ±10% | Equipment must not reduce energy efficiency or increase operating cost substantially | Selection sheet and efficiency data | Higher operating costs
Interoperability / Compatibility | Equal or superior only | 0% negative deviation | Similar equipment must remain fully compatible with specified systems, approved interfaces, communication protocols, software/firmware requirements, without requiring material redesign or reduction of functionality. | Datasheets and interoperability/compatibility statement | Integration failures and loss of system functionality
Testing / commissioning / as-built | Mandatory | 0% deviation | Required protocols, measurements, labels, cause-effect tests, training and handover documents must be delivered | Test reports and as-built files | Unverifiable installation / claims
Compartment-specific recommendations
Compartment | No negative deviation / critical parameters | Parameters with possible margin | Specific evaluation rule | Evidence required | Approval note
SA_MASI | EI/E/EW classes, reaction to fire, acoustic performance, complete door/fire-stop assembly certification, evacuation compatibility | Dimensions ±5%; weight ±10% where supports and openings remain adequate | Equivalent doors/fire-stopping only as complete tested assemblies; finishes require same quality/fire/durability class | Certificates/test reports, datasheets, samples if requested | Designer/Employer approval for alternatives affecting MASI
RAC | Flow/head, pressure class, potable suitability, fire-hydrant function, materials for hydraulic duty | Power +10% or +0.02 kW for small loads; dimensions ±5%; weight ±10% | Pumps evaluated by Q/H curve and duty point, not motor power alone | Pump curves, datasheets, test/commissioning protocols | Hydraulic/fire-safety function cannot be downgraded
IVC | Airflow, pressure, useful capacities, smoke-control duty, filtration, efficiency/SFP/COP/EER | Capacity +10…15% if balanced; dimensions ±5%; weight ±10%; noise max +3-5 dB(A) | Smoke-control fans/equipment cannot be replaced by ordinary HVAC equipment | Selection sheets, certificates, acoustic/energy data, balancing protocol | Designer/Employer approval for smoke-control alternatives
EEF_IEI | Rated current, breaking capacity, RCD/SPD, selectivity, CPR/FE/E cable class, autonomy, IP/IK, earthing | Small load power +10% or +0.02 kW; panel dimensions ±5% if fit/access maintained | Electrical equivalence must match approved diagrams and protections | Datasheets, certificates, load/protection checks, test reports | No lower cable class or emergency autonomy
SI_SIn | EN54/EN12094/EN12101, CPR/CoP/DoP, compatibility, loop protocol, isolators, autonomy, gas calculation, cause-effect | Dimensions ±5%; weight ±10%; small loads +10% or +0.02 kW if autonomy remains compliant | Gas extinguishing alternatives require recalculation and certified compatible components | Certificates, compatibility matrix, gas calculation, I/O list, test protocols | No unapproved change to agent/concentration/cylinders/control logic
SCA | Controlled doors/readers, fire-release logic, evacuation compatibility, autonomy, event logging, local administration | Lock force equal/higher if door suitable; small load power +10%/+0.02 kW; reader dimensions ±10% | Cloud-dependent or P2P-only systems not accepted unless approved | Datasheets, wiring diagrams, cybersecurity/data protection notes | Fire/evacuation interface must be tested
CCTV | Resolution, number of cameras, FOV/lens, low-light, IP/IK, NVR capacity, PoE, local recording/export, retention | Higher resolution accepted only if NVR/network/storage fit; PoE +10% if budget sufficient; dimensions ±10% | Retention proven by calculation, not by HDD size alone | Camera/NVR/HDD/switch datasheets, retention calculation, commissioning records | No mandatory cloud/P2P unless approved
TS_SCS | Category, CPR/reaction-to-fire class, number of ports, rack capacity, testing/labels | Cat.6 accepted instead Cat.5e only as complete compatible channel; dimensions ±5%; quantities only via approved/as-built routes | Each permanent link/channel must be tested and labelled | Component datasheets, CPR certificates, test reports, as-built port schedule | No lower category or untested ports